ANDHRA PRADESH POWER GENERATION CORPORATION LIMITED

Dr.Narla Tatarao Thermal Power Station

* * * * *

Notice Inviting Tender (NIT) No.E-25/2026-27/CE/O&M/Dr.NTTPS(O&M/Stage-V)

Tender Specification No: 708/2026-27/CE/O&M/Dr.NTTPS (SE/O&M/Stage-V)

BIDDING DOCUMENTS FOR THE WORK OF

“Carrying out of Preventive / Break-down / Overhauling Maintenance works of ID, FD, PA, Seal Air & Scanner Air Fans during the year 2026-27.”

I N D E X

| Sl. No. | Description | Page No. |
| --- | --- | --- |
| 1 | Summary Sheet | 3 |
| 2 | Tender Form | 4 |
| 3 | Detailed Tender Notice | 05 - 06 |
| 4 | Bid Qualifying requirements | 07-08 |
| 5 | Schedule of Rates & Quantities | 09 |
| 6 | UNDERTAKING II | 10 |
| 7 | Section-II (Scope of Work) | 11 |
| 8 | GST Annexure for BOQ | 12 |
| 9 | General terms & Conditions | Separate File attached |
| 10 | Section-III (Schedule- Bill of Qty’s) | Separate File attached |
| 11 | Section-IV (SCHEDULE) | Separate File attached |

| ANDHRA PRADESH POWER GENERATION CORPORATIONLIMITED |  |  |  |
| --- | --- | --- | --- |
| DR NARLA TATA RAO THERMAL POWER STATION |  |  |  |
| Specification No. 500/2026-27 CE/O&M/Dr.NTTPS(Stage-V) |  |  |  |
| (SUMMARY SHEET) |  |  |  |
| (1) | Name of the work | : | Carrying out of Preventive / Break-down / Overhauling Maintenance works of ID, FD, PA, Seal Air & Scanner Air Fans during the year 2026-27. |
| (2) | Contents of the Specification | : | 1. Section – I(A) : General Conditions 2. Section – I(B) : Safety Clauses 3. Tender Form 4. Schedule of Rates & approximate Qty's 5. Undertaking-I & Undertaking-II 6. Proforma of BG for the Security Deposit (SD) 7. Section-II : Scope of work 8. Section-III : Schedule & subsequent Annexure |
| (3) | Officer to whom Tender shall be addressed | : | The Chief Engineer/O&M, Dr.NTTPS/Ibrahimpatnam-521456. |
| (4) | Last date for downloading of Tender Specification | : | 10.00 Hrs on 28.10.2026 |
| (5) | Last date and time of receipt of Tender Specification | : | 11.00 Hrs on 28.10.2026 |
| (6) | Date and time of opening of bid |  | 11:30 Hrs on 28.10.2026 |
| (7) | Place of opening | : | O/o. Superintending Engineer/O&M/Stage-V/Dr.NTTPS. |
| (8) | EMD to be paid | : | ₹ 7,010.00 for those who are not having PEMD of Rs.5,00,000.00 Lakh with APGENCO. |
| (9) | Security deposit | : | 2.5% of the tendered value. |
| (10) | Period of completion of work | : | The work shall be taken up and completed as per the instructions of the Executive Engineer/BM & AHP/ Dr.NTTPS |
| (11) | Telephone numbers | : | 0866-2882301 |
| (12) | Mail ID | : | seemstg5nttps@gmail.com |
| (13) | Terms of payment | : | As per the Clause No’s (62 to 64) of Section-I(A) attached here with |

TENDER FORM

To

The Superintending Engineer,

O&M, Stage-V, Dr.NTTPS, Ibrahimpatnam,

Krishna District – 521 456.

Sir,

I/We do hereby tender and, if this tender be accepted undertake to execute the work of Carrying out of Preventive / Break-down / Overhauling Maintenance works of ID, FD, PA, Seal Air & Scanner Air Fans during the year 2026-27.as described in the specifications deposited in the office of the Superintending Engineer/O&M/Stg-V/Dr.NTTPS, Ibrahimpatnam, KRISHNA DISTRICT – 521 456, with such variations by way of, alterations or additions to, and omissions from the said work and method of payment as are provided for in the “Conditions of Contract” at the estimated contract value (ECV) PLUS (or) MINUS % or such other sum as may be arrived at under the clause of the standard preliminary specification relating to “Payment on lump sum basis or final measurements at unit prices”.

I/We agree to execute the work when the lump sum payment under the terms of agreement is varied by payment on measurement quantities.

I/We agree to keep the offer in this tender valid for a period of 120 days from the date of opening of tender and not to modify the whole or any part of it for any reason within the above period. If the tender is withdrawn by me/us for any reason whatsoever, within the validity period, the earnest money deposited by me/ us will be forfeited to APGENCO.

I/We hereby distinctly and expressly declare and acknowledge that before the submission of my/ our tender, I/We have carefully followed the instructions in the tender notice and have read the APSS and the Preliminary specifications therein and the APSS Addenda volume; and that I/We have made such examination of the contract documents and of the plan, specifications and quantities, and of the locations where the said work is to be done, and such investigation of the work required to be done, and in regard to the materials required to be furnished so as to enable me/us to thoroughly understand the intention of the same and the requirements, covenants, agreements, stipulations and restrictions contained in the contract and in the said plans and specifications and distinctly agree that I/We will not hereafter make any claim or demand upon the APGENCO based upon or arising out of any alleged misunderstanding or misconception or mistake on my/our part of the said requirements, covenants, agreements, stipulations restrictions and conditions.

If our tender is not accepted, this sum shall be required to us on our application when intimation is sent to me of rejection or at the expiration of three months from the date of this tender whichever is earlier.  If our tender is accepted, the earnest money shall be retained by Andhra Pradesh Power Generation Corporation Limited as Security for the due fulfillment of the contract.

If, upon written intimation to us by the Superintending Engineer/O&M/Stage-V/ Dr.NTTPS, we fail to attend the said office before the end of the period specified on such intimation the tenders will not be considered and if, upon intimation being given to us by the Superintending Engineer/O&M/Stage-V/DR.NTTPS/Ibrahimpatnam of acceptance of our tender, we fail to enter into the required agreement as defined in relevant clause of the detailed tender notice, then we agree to the forfeiture of the Earnest Money.  Any notice required to be served on us by post (Registered or Ordinary) or left at our address given herein.  Such notices shall if sent by post be deemed to have been served on us at the time when in due course or post if would be delivered at the address to which it is sent.

I/We fully understand that the written agreement to be entered into between us and the Andhra Pradesh Power Generation Corporation Limited shall be the foundation of the rights of both the parties and the contract shall not be deemed to be complete until agreement has first been signed by us and then by proper officer authorized to enter into contracts on behalf of Andhra Pradesh Power Generation Corporation Limited.

Yours faithfully,

T E N D E R E R

DETAILED TENDER NOTICE

Tenders for the work of “Carrying out of Preventive / Break-down / Overhauling Maintenance works of ID, FD, PA, Seal Air & Scanner Air Fans during the year 2026-27.”  should be in the prescribed form which can be obtained from ‘e’ procurement platform from the date of electronic publication up to the time and date indicated in the tender notice. The intending bidders shall enroll themselves on the ‘e’ procurement market-place www.apeprocurement.gov.in. Those contractors who register themselves in the ‘e’ procurement market place can download the tender schedules free of cost. The bidder shall authenticate the bid with his digital certificate for submitting the bid electronically on e-procurement platform and the bids not authenticated by digital certificate of the bidder will not be accepted on the e-procurement platform following the G.O.Ms.No.6, I.T&C Department, Dated:28-02-2005.

- The intending bidders can download tender specification and submit their tenders online at e-procurement market place viz., www.apeprocurement.gov.in. The tender forms can be downloaded upto 10:00Hrs on 28.10.2026. Bids can be submitted up to 11:00hrs on  28.10.2026.

- The bids will be opened through e-procurement platform by the Superintending Engineer /O&M/Stage-V/Dr.NTTPS  on   28.10.2026  at 11:30 Hrs  in his chambers, Stage-V, Dr.NTTPS, Ibrahimpatnam, Krishna Dist. -521 456. If the tender opening day happens to be a holiday the tenders will be opened at the same timings mentioned above on the next working day. The tenderers or their authorized agents are expected to be present at the time of opening of tenders.

- Intending bidders can contact office of the Superintending Engineer/O&M/Stage-V, Dr.NTTPS, Ibrahimpatnam, Krishna Dist. 521 456 for any clarification / information on any working day during working hours.

- The bidders who are desirous of participating in e- procurement shall submit their Technical bid/ Price bid etc., in the standard formats prescribed in the tender documents, displayed at “e” market place. The bidders should invariably upload the statement showing the list of documents etc., in the “e” market place in support of their Technical bids. The bidder should upload scanned copies of all relevant certificates. The bidder shall sign on all the statements, documents, certificates, uploaded by him, owning responsibility for their correctness/authenticity. Responsibility for correctness of the information submitted in the online bid lies with bidder.  If any information furnished in the bid is proved to be false at a later date, the bid will not only be rejected but the bidder will be BLACKLISTED.

- The bidder has to furnish the following statutory requirements along with the bid.

- Income tax Clearance Certificate: The contractor shall furnish their copy of Permanent Account Number (PAN) card and copy of latest income tax returns submitted along with the proof of receipt.

- GST Registration Certificate:  The tenderer should furnish the proof of registration under GST from the Commercial tax department.

- EPF & ESI: The contractor shall comply with the statutory labour rules and regulations i.e., EPF, ESI etc., as may be applicable and shall furnish the returns and information as may be specified from time to time.  Bills will not be processed without fulfilling these statutory norms.

- Valid Labour License

- Solvency certificate: Solvency certificate or  Net worth certificate  shall be submitted  to know the financial status of the previous year of the  firm/company  along with the tenders ,  failing which tenders will be rejected.

- Solvency Certificate (  100% of the Estimated Contract Value) from any Nationalized/ Scheduled bank and not older than one year from the date of participating in tender (or) the NET WORTH  certificate  issued by a  registered Chartered account  (along with registered seal) in lieu of solvency certificate can also  be submitted. These certificates should include the latest  financial year  turnover ( For  tenders  floated on or before  01-10-2026  turnover of the year 2024-25 should be certified and for tenders  floated after  01-10-2026  turnover of the year 2025-26  should be certified.)

- Each tenderer shall invariably upload the required registration, experience certificates, solvency and insurance coverage for the workmen. In case of proprietary or partnership firm, it will be necessary to produce the certificates afore mentioned for the proprietor or proprietors and for each of the partners, as the case may be.

- Earnest Money Deposit: Each bidder must pay Bid Security i.e., Earnest Money Deposit of ₹ 7,010.00 for those who are not having prescribed PEMD with APGENCO and ₹    0.00 for those who are having prescribed PEMD with APGENCO. Payment of EMD should be done by Electronic Payment Gateway accepts all Master and Visa Credit Cards issued by any bank and Direct Debit facility/Net Banking of ICICI Bank, HDFC, Axis Bank to facilitate the transaction. The bidders shall also upload in the e-procurement web site the scanned copies of reference approved letter of PEMD deposited with APGENCO if applicable.

Further registered SC/ST/vaddera Societies and individuals belonging to unemployed SC/ ST/ vadderas) shall Upload a declaration about the works on hand for claiming exemption towards EMD (Vide GO Ms Ns.52 Dt.18-03-2000) while submitting their bids.

Exemption from payment of EMD for SSI/NSIC Units: Registered SSI Units or the MSE (MSEs) with  NSIC  registered under Single point Registration Scheme (SPRS) by the Dept of Industries/Govt. of AP are eligible for exemption from payment of EMD, subject to the following conditions. SSI acknowledgement is not accepted.

- The list of Items - for which the Firm is registered, must be relevant to the tendered items.

- The quoted price shall be less than the monetary limit stipulated in the Registration Certificate unless otherwise the Certificate issuing Authority has clearly mentioned in the Certificate as “Exempted from deposit of Earnest Money irrespective  of value of Monetary Limit.

- The BIDDERS who fulfill the above conditions shall upload a copy of valid Certificate of Registration either with NSIC indicating details such as Monetary Limit, details of items covered in the registration, validity period of Certificate etc. However, please note that exemption will be considered purely at APGENCO’s discretion.

The EMD will not be received in cash. The Earnest Money will be retained in the case of successful tenderer and will not carry any interest. It will be dealt with as provided in the tender.

- PARTICIPATION IN TENDER IS OPEN TO THOSE CONTRACTORS WHO FULLFILL THE FOLLOWING:

    - Should have registered with Regional Provident Fund Commissioner and having independent E.P.F Code Number.

    - Should possess valid independent ESI Code number.

    - The Labour license (obtained from labour department) should be valid & same shall be furnished before the date of commencement of work invariably.

    - Should have registered with GST cell and posses GST registration number.

    - Should posses PAN Number

    - The tenderer should furnish Solvency certificate-- Solvency Certificate (100% of the Estimated Contract Value) from any Nationalized/ Scheduled bank and not older than one year from the date of participating in tender (or) the NET WORTH  certificate  issued by a  registered Chartered account (along with registered seal) in lieu of solvency certificate can also  be submitted.These certificates should include the latest  financial year  turnover (For  tenders  floated on or before  01-10-2026  turnover of the year 2024-25 should be certified and for tenders  floated after  01-10-2026  turnover of the year 2025-26  should be certified.).

    - The Tenderer Should have experience in carrying out this type of works in 210MW Thermal plant (or higher rating) atleast once in  last 6 financial years including present financial year and shall have satisfactory completion certificate to that effect.

- If last date of tender opening happens to be a Public Holiday the same will be opened on the next working day at the same time and place. The undersigned reserves the right to reject any tender in full or part or all the tenders without assigning any reason.

- The CE/O&M/Dr.NTTPS or other competent sanctioning authority reserved the right to suitably modify the period of work to be awarded to the Contractors/Agencies to suit departmental requirements.  No objections or correspondence will be entertained in this matter.

BID QUALIFYING REQUIREMENTS

The Contractor should invariably furnish details and submit Photostat copies:

    - The Tenderer Should have experience in carrying out this type of works in 210MW Thermal plant (or higher rating) atleast once in  last 6 financial years including present financial year and shall have satisfactory completion certificate to that effect.

    - The contractor or his authorized representative should reside within the premises of Ibrahimpatnam and he should be made available over phone all the time during the period of execution of Contract i.e. from the date of issuing P.O. to the last date of satisfactory completion of work.

    - Firm Registration certificate: The contractors/ Firms  possessing “Registration of Firms”  Certificate  or  any of the   registrations like  MSME registration , EPF & ESI Registration, GST Registration ,  Labour License   certificate  shall be considered as “ Firm Registration”  and are eligible for  participating in Tenders.

However, “Registration of Firms” certificate is Mandatory in case of  Partnership firms  and they shall submit a copy of the document for participating in tenders.

In case of participation of  tenders in Civil works, The contractor or Firm should mandatorily produce Contractor  registration certificate obtained  from APGENCO or from any  Government organization failing which will be  rejected.

    - Goods & Service tax registration: The contract shall furnish a copy of Goods & Service tax registration certificate.

    - Income tax clearance certificate: The firm shall furnish a copy of valid PAN card and latest income tax returns submitted along with proof of receipt. In case of proprietary or partnership firm it will be necessary to produce the aforesaid certificate for the proprietor or proprietors and for each of the partners, as the case may be. If a certificate had already been produced by the tenderer during the calendar year in which the tender is made in respect of any previous tender submitted to this office, it will be sufficient if particulars regarding previous occasion on which the certificate was produced are given.

    - EMD (Bid Security): The tenderer should furnish an EMD of ₹ 7,010.00 Pay as per the payment options available in the E-procurement platform and Payment of EMD should be done by Electronic Payment Gateway accepts all Master and Visa Credit Cards issued by any bank and Direct Debit facility/Net Banking of ICICI Bank, HDFC, Axis Bank to facilitate the transaction.

Note:

  - In case of Permanent E.M.D Holders, ₹ 7,010.00. Online payment as per the payment options available in the E-procurement platform plus copy of the P.E.M.D approval letter from APGENCO may be furnished.

Exemption from payment of EMD for SSI/NSIC Units: : Registered SSI Units or the MSE (MSEs) with  NSIC  registered under Single point Registration Scheme (SPRS) by the Dept of Industries/Govt. of AP are eligible for exemption from payment of EMD, subject to the following conditions. SSI acknowledgement is not accepted.

- The list of Items - for which the Firm is registered, must be relevant to the tendered items.

- The quoted price shall be less than the monetary limit stipulated in the Registration Certificate unless otherwise the Certificate issuing Authority  has clearly mentioned in the Certificate as “Exempted from deposit  of Earnest Money irrespective  of value of Monetary Limit..

- The BIDDERS who fulfill the above conditions shall upload a copy of valid Certificate of Registration either with NSIC indicating details such as Monetary Limit, details of items covered in the registration, validity period of Certificate etc. However, please note that exemption will be considered purely at APGENCO’s discretion.

- Solvency certificate: A)     Solvency certificate or Net worth certificate shall be submitted  to know the financial status of the   firm/company  along with the tenders ,  failing which tenders will be rejected.

B) Solvency Certificate ( 100% of the Estimated Contract Value ) issued by  Nationalized/ Scheduled bank and not older than one year from the date of participating in tenders  (or) the NET WORTH  certificate  issued by a  registered Chartered account (along with registered seal) in lieu of solvency certificate can also  be submitted. These certificates should include the latest  financial year  turnover (For  tenders  floated on or before  01-10-2026  turnover of the year 2024-25 should be certified and for tenders  floated after  01-10-2026  turnover of the year 2025-26  should be certified.).

(8)  Validity of Tender: The tenderer should be kept valid for 120 days from the date of

Opening of price bids.

    - Registration certificates: The tenderer shall furnish a copy of registration certificates EPF, ESI, Labour License, PAN, and GSTIN registrations.

    - The Labour license (obtained from labour department) should be valid & same shall be furnished before the date of commencement of work invariably (or) shall furnish undertaking if labour license is not applicable .

    - The contractor shall have good track record in their works and they should not be black listed at any where, in the tender period. The contractor shall submit undertaking mentioning that the firm is not a black listed firm at the time of quoting of tenders.

    - Details of the schedules to be filled and submitted by the tenderer along with the tender.

SCHEDULE OF RATES AND APPROXIMATE QUANTITIES

- The quantities given are those given upon which lump sum tender cost of the work is based but they are subject to alterations, omissions, deductions or additions as provided for in the conditions of the contract and do not necessarily the show the actual quantities of the work to be done. The rates noted below are those governing payment for extra for additions or commissions according to the conditions of the contract as set forth in the preliminary specification of AP.GENCO- APDSS of the contract.

- It is to be expressly understood that the measured work is to be taken out (not withstanding any customs or practice to be Contrary) according to the actual quantities when in place and furnished accordingly to the drawing or as may be ordered from time to time by the Executive Engineer/BM&AHP/Dr.NTTPS. And the cost calculated by measuring or weight at the respective prices without any additional charges for any necessary or contingent works there with. The rates quoted or for works in site complete, in every respect and are firm not subject to adjustment with variation in cost of labor, materials on any other factors affecting prices and services

- For all items of work which are more than 10% in excess of the quantities shown in the bill of quantities the rate payable for the Excess quantities beyond 10% shall be either tender rate or the SS rates for the plus or minus the overhaul tender percentage whichever is less. This rates means the rates with which the estimate has been prepared for comparison with tenders.

Signature of the Contractor

UNDERTAKING-II

It is to confirm that, we - our firm/contractor is not under blacklisted condition in anywhere as on date. Further, we are hereby confirming our acceptance to all the Terms & Conditions attached to this Tender Specification.

SIGNATURE OF THE CONTRACTOR

SCOPE OF WORK

| Name of the Work: | “Carrying out of Preventive / Break-down / Overhauling Maintenance works of ID, FD, PA, Seal Air & Scanner Air Fans during the year 2026-27.” |
| --- | --- |

Scope of Work :

TLT-Turbo, Germany Design, Axial Flow Type FD Fans (Model: FAF 26/12.5-1), PA Fans (Model: PAF 20/11.2-2) and ID Fans(Model: SAF 39.8/21.2-2).

1.Cleaning of the ducts and Fan internals.
i) Arranging temporary scaffolding for areas of higher elevations.
ii) Cleaning of the suction chamber, bullet, covers, blades, diffuser and discharge up to the secondary air damper.

2.Cleaning of the silencer and painting of the suction mesh.

i) Making arrangements to go up the areas of higher elevation.
ii) Opening of the manual door provided in the suction mesh and removing of the washed material struck up in the mesh.
iii) Cleaning of the suction mesh thoroughly with wire brushes and compressed air.
iv)Painting of the suction mesh, suction hood roof with bituminous black paint.
v)Cleaning of the silencer with compressed air.
vi)Closing of the manual door.

3.Servicing of lube oil unit and changing of lube oil.

i) Draining the oil from the tank, filters and coolers and collecting the oil into barrels.
ii) Cleaning the tank, filters and oil coolers and flushing and Hydraulic testing of lube oil coolers and rectifying the tube leaks if any.
iii) Servicing the coolers, valves.
iv) Flushing of all lube oil pipe lines with compressed air.
v) Painting of the lube oil unit with enamel paint for outside and oil resistant paint for inside of the lube oil tank.
vi) Filling the lube oil tank with fresh oil of Servo prime-68.
vii)Arresting of oil leaks in the equipment.
viii)Trail operation of the lube oil unit and keeping oil in circulation and arresting oil leaks if any.

4. Replacement of Hydraulic Adjustment Device (HAD), and alignment with hub of impeller

i. Opening of access door of delivery side of bullet casing to enter into HAD (Hydraulic adjustment device) chamber
ii. Cleaning of ash settled inside of delivery side of bullet casing

iii. Opening of access door of HAD chamber
iv. Cleaning inside HAD chamber if there is any oil traces
v. Check for any loosen connection/oil leakage in Pressure oil Hydraulic line (PH), Return oil Hydraulic line (RH) and Leakage oil
Hydraulic line(LH) inside HAD chamber and outside lines of HAD chamber, and mark them by LOP(lube oil pump) kept in service.
vi. Check for any loosen connection/oil leakage in Pressure oil line of main bearing (PL), Return oil line of main bearing (RL) and
Pressure Equalization line of main bearing (EL) inside fan and around the main bearing chamber and outside lines and mark them.
vii. Check for any loosen connection/oil leakage in Pressure oil line of motor bearing -1&2, Return oil line of motor bearing -1&2 and mark them..
viii. Check for any loosen connection/oil leakage in lube oil skid
ix. Stop LOPs and remove any loosen connection/oil leakage found and marked in above said lube oil lines and change/replace if any damaged male/female connectors, flexible hoses ,elbows, unions found or tighten those joints by using proper tools.
x.. Replacement of HAD if existing one is problematic.
xi. After replacement/tightening of any damaged male/female connectors, flexible hoses, elbows, unions, Check for any oil leakages
in above said lines by duly LOPs kept in service and continuous operation of blade pitch(Fan motor and rotor must be in OFF condition).
xii. Ensure there are no oil leakages inside and outside of Fan and lube oil skid before boxing up the fan after completion of work.
xiii. Close the HAD chamber, access door of delivery side of bullet casing and access door of the diffuser after proper inspection by departmental engineer.
xiv. Inspection of Rotor Assembly and carrying-out of rectification if any abnormalities
xv. Inspection of Blades and carrying-out of rectification if any abnormalities
xvi. Inspection of Sealing and Cooling Blower System lines of both Main Bearing & HAD Chambers and carrying-out of rectification if any abnormalities
xvii. All consumables and T&P for above said work are in contractor scope.
xviii. Attending of connected works if any.

5.Dismantling and Assembling of upper half of Fan Casing.
i)Marking of mating joints, removing of bolts and opening of man hole doors of fans.
ii)Dismantling of expansion bands at both ends of the fans.
iii)Making arrangements to lift off the upper casing of the fan with the help of hoist/chain pulley blocks.
iv)Removing of the upper casing without contacting to impeller blades.
v)Cutting the gaskets and cleaning of dismantled parts and fasteners.
vi)Assembling of the upper casing as per the markings.
vii)Care should be taken to avoid contact with impeller blades.
viii)Securing of the upper casing with fasteners.

6. Checking and Correcting the alignment of Fan and Motor.
i)Checking and alignment of the Coupling, Motor, Fan & HAD and correcting the alignment of Motor, Coupling, FAN & HAD, if any deviation observed after trail rotation of the fan.
ii)Mounting and fixing of bullet cover upper half.
iii)Re-fixing of shaft protecting tube.
iv)Cleaning of suction chamber without any foreign material in it.

Seal Air Fans & Scanner Air Fans.

1.Cleaning of Impeller Spiral Casing and Fan Internals.
i) Cleaning and removing of the ash deposits.
ii) Checking inside the spiral casing from suction side expansion joints (inlet guide vanes) to the delivery side expansion joints.
iii) Cleaning of the impeller, fan shaft and suction cones.
iv) Arresting the air leaks from the impeller spiral casings/housings. v) Alignment of fan rotor and motor and replacement of bearing oil if necessary.

2.Dismantling, Overhauling and assembling of impeller and shaft with bearing assembly.
i) Drain the oil from the bearing housing.
ii) Dismount labyrinth seal assemblies.

iii) Remove fasteners in the horizontal and vertical flange joints of
upper quadrant of the spiral casing.
iv) Pull and slide out the spiral causing quadrant and remove.
v) Remove the shaft with bearing housing connecting bolts.
vi) Remove the shaft with bearing assembly along with the impeller and position it on a suitable stand.
vii) Cleaning of all dismantled parts.
viii) Checking and changing of worn out parts like bearing, sleeves, oil seals etc.
ix) After overhauling the impeller and bearing assembly, re-assemble the rotor assembly.

3.Servicing of suction damper.
i) Disconnecting the connecting levers of 4 Flap damper control assemblies of Seal Air Fans.

ii) Clearing of dust & lubricating the bearing housing areas on both sides of the suction dampers.
iii) Assembling the connecting levers of 4 Flap damper control assemblies.
iv) Ensuring the free movement (opening & closing) of both the 4 Flap suction dampers.

4.Opening of Inspection cover of flap gate, cleaning the internals ensuring free operation and replacing the same if necessary.
i) Arrangement of Scaffolding at the inspection cover of seal air fans discharge flap gate.
ii)Removal of fasteners for manhole door of the flap gate.
Iii) Removing of dust, ash at the flap gate seating areas & bearing housing areas.
iv) Lubricating the bearing housing areas on both sides of the flap gate.
v) Ensuring the free movement (opening & closing) of the flap gate on both the sides.
vi) Assembling of fasteners for manhole door of the flap gate.
vii) Dismantling of Scaffolding at the inspection cover of seal air fans discharge flap gate.

5.Dismantling and assembling of upper half of impeller casing and discharge/suction ducts.
i) Transporting required T & P to the location from sub division stores.
ii)Marking of mating joints, removing of bolts and opening of observation doors of Seal Air fans.
iii) Making arrangements to lift off the upper casing of the fan with the help of chain pulley blocks.
iv) Removing of the upper casing without contacting to impeller.
v) Cutting the gaskets and cleaning of dismantled parts and fasteners.
vi) Assembling of the upper casing as per the markings after arranging the gaskets.
vii) Care should be taken to avoid contact with impeller.
viii) Securing of the upper casing with fasteners.
ix) Transporting T & P from the location to sub division stores.

6. Cleaning of suction air filters / Dyna vane Filter and arresting of air leaks.

i) Transporting required T & P to the location from sub division stores.
ii) Erecting of temporary platforms around the Dyna vane filter of Seal air fan.
iii) Dismantling the suction, discharge and drain flanges of Dyna vane filter.
iv) Cleaning of the filters with service air and replacing of the damaged flange gaskets with new ones for arresting the air leaks.
v) Assembling back the suction, discharge and drain flanges of Dyna vane filter.
vi) Dismantling of temporary platforms.
vii) Transporting T & P from the location to sub division stores.

7. Checking the bearing clearances and alignment of fan and motor.

i) Transporting required T & P to the location from sub division stores.
ii) Draining of lube oil from bearing housing.

iii) Opening of the bearing housing end cover flanges.
iv) Inspection of the bearing clearances
v) Closing of Bearing housing end cover flanges.
vi) Filling of bearing housing with new lube oil.
vii) Making the arrangements of dial indicators.
viii) Checking the alignment of fan and motor.
ix) Correcting the alignment reading if necessary.
x)Transporting T & P from the location to sub division stores.

Sd/-xxxxxxxx

Chief Engineer/O&M/Dr.NTTPS

Signature of the Tenderer

GST ANNEXURE

NOTE :

In order to implement the GST Act, It is hereby requested to furnish the HSN/SAC codes along with applicable % of GST for the goods/services in the following annexure Please.

| Sl. No | Description | SAC / HSN Codes under GST | Applicable % GST |
| --- | --- | --- | --- |
| 1 | Cleaning of the ducts and fan internals. |  |  |
| 2 | Cleaning of the silencer and painting of the suction mesh. |  |  |
| 3 | Servicing of lube oil unit and changing of lube oil pump. |  |  |
| 4 | Opening of bullet cover and dismantling of pipe lines and closing |  |  |
| 5 | Replacement of Hydraulic Adjustment Device (HAD), and alignment with hub of impeller. |  |  |
| 6 | Overhauling of 1 no. blade bearing assembly. |  |  |
| 7 | Overhauling of impeller(rotor) assembly. |  |  |
| 8 | Servicing/overhauling of main bearing assembly |  |  |
| 9 | Dismantling and assembling of upper half of fan casing. |  |  |
| 10 | Checking & correcting the alignment of Fan and motor. |  |  |
| 11 | Cleaning of the ducts and fan internals. |  |  |
| 12 | Cleaning of the silencer and painting of the suction mesh. |  |  |
| 13 | Servicing of lube oil unit and changing of lube oil. |  |  |
| 14 | Replacement of Hydraulic Adjustment Device (HAD), and alignment with hub of impeller. |  |  |
| 15 | Overhauling of 1 no. blade bearing assembly. |  |  |
| 16 | Overhauling of impeller(rotor) assembly. |  |  |
| 17 | Servicing/overhauling of main bearing assembly. |  |  |
| 18 | Dismantling and assembling of upper half of fan casing. |  |  |
| 19 | Checking & correcting the alignment of Fan and motor. |  |  |
| 20 | Cleaning of the ducts and fan internals. |  |  |
| 21 | Servicing of lube oil unit and changing of lube oil. |  |  |
| 22 | Opening of bullet cover and dismantling of pipe lines and closing. |  |  |
| 23 | Replacement of Hydraulic Adjustment Device (HAD), and alignment with hub of impeller. |  |  |
| 24 | overhauling of 1 no. blade bearing assembly. |  |  |
| 25 | Overhauling of impeller(rotor) assembly. |  |  |
| 26 | Servicing/overhauling of main bearing assembly. |  |  |
| 27 | Dismantling and assembling of upper half of fan casing. |  |  |
| 28 | Checking & correcting the alignment of Fan and motor. |  |  |
| 29 | Rectification of control oil leakage from HAD inside chamber and arresting of all lube oil line leaks, internal inspection of Fan. |  |  |
| 30 | Cleaning of impeller spiral casing and fan internals. |  |  |
| 31 | Dismantling, overhauling and assembling of impeller and shaft with bearing Assembly. |  |  |
| 32 | Servicing of suction dampers of Seal Air Fans. |  |  |
| 33 | Opening of inspection cover of flap gate, cleaning the internals ensuring free operation and replacing the same if necessary. |  |  |
| 34 | Dismantling and assembling of upper half of impeller casing and discharge/suction side ducts/rubber expansion Joints. |  |  |
| 35 | Cleaning of suction air filter(Dynavane) and arresting of air leaks. |  |  |
| 36 | Checking the bearing clearances and alignment of fan and motor |  |  |
| 37 | Cleaning of impeller spiral casing and fan internals. |  |  |
| 38 | Opening of inspection cover of flap gate, cleaning the internals ensuring free operation and replacing the same if necessary. |  |  |
| 39 | Checking the bearing clearances and alignment of fan and motor. |  |  |

The above annexure shall be uploaded along with the E-Tender for implementing GST .

Sd/-x x x x x x                                                                                                                                                                    CHIEF ENGINEER

SIGNATURE OF THE TENDERER					O&M/Dr.NTTPS