## Schedule
ANDHRA PRADESH STATE ROAD TRANSPORT CORPORATION
Bill of quantites
TENDER SCHEDULE- A (PART-I)
Name of work: Providing Electrical Infrastructure to Intermediate Charging Station at Adoni Bus Station, Kurnool District (3rd Call).
No. of Items: 61 (Sixty One only)
Sl | PROBABLE |  | DESCRIPTION OF WORK | APDSS | UNIT IN | RATE | AMOUNT
No | QUANTITY |  |  |  | FIGs &
|  |  |  | SS NO | WORDS | Rs. Ps. | Rs.
(1) | (2) |  | (3) | (4) | (5) | (6) | (7)
1 | 25.3 | Cum | EARTH WORK EXCAVATION in all kinds of soils wet or dry such as clay, hard clay, black cotton soil, red earth, moorum, gravel etc., in loose and slushy conditions except rock requiring blasting for foundation of walls and column footings with necessary site clearance, marking out temporary stepping,sloping,shoring, strutting sectioning, tamping as directed with an initial lead of 10M and lift of 3M, etc., including cost and conveyance of all labour and materials , all incidental and operational charges etc complete as directed by the Engineer-in-charge. | SS | 1Cum (One Cubic metre) | 395.4 | 10004
2 | 2 | Nos | Supply and transportation of 9.0 M length 150X150 mm RS Joist poles ( Wt of pole 333 Kgs ) including cost and conveyance of all labour and materials , all incidental and operational charges etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 28375.4 | 56751
3 | 23 | Cum | Refilling of excavated earth in Foundations and Basement including spreading in layers watering compaction including cost and conveyance of all labour and materials , all incidental and operational charges etc., complete as directed by Engineer in charge. | SS | 1Cum (One Cubic metre) | 43.8 | 1007
4 | 4 | Hrs | Hire charges for engaging of 16 Tonne capacity Crane for erection of RS Joist poles and VCBs including hire charges of Crane, Fuel, crew charges, etc., including cost and conveyance of all labour and materials , all incidental and operational charges etc., complete as directed by Engineer in charge. | SS | 1 Hr (One Hour) | 5619 | 22476
5 | 890 | Kgs | Supply,fabrication and Erection of the Mild Steel Members MS Chanels /Angles/ Beams /MS Flat including cost of welding, wastages,fabrication charges and erection charges, cost and conveyance of all labour and materials, all incidental, operational and scaffolding charges etc., complete as directed by the Engineer-in- Charge (for finished item of work) | SS | 1 KG ( One kilo gram) | 129.9 | 115611
6 | 50 | Kgs | Supply,transportation and fixing of MS Bolts,Nuts and Washers including cost of all materials and labour charges etc ., as directed. | SS | 1 Kg ( One Kilo Gram) | 139.2 | 6960
7 | 1 | No | Supply and fixing of 11 KV,400 Amp 3 phase central post rotating double breack type AB switch (isolater) as per IS 9921 with out earth blade,gang operated, Horizontal type, operating mechanism with GI spring loaded reverse loop type fixed contact with silver/Nickel plated at end points,9Nos post insulators of 12KV(IS2594 and IS 5350),Hot Dip galvanizing hardware,GI pipe,Nuts and bolts etc.,including cost and conveyance of all labour and materials , all incidental and operational charges etc complete as directed by the Engineer-in-charge. | SS | 1No (Each) | 24745.3 | 24745
8 | 3 | Nos | Supply and fixing of distribution type lightning arresters 11KV,5kA as per IS 3070 with mounting base on the existing DP stucture including cost of all materials and labour charges etc.,as directed by the Engineer-in-charge. | SS | 1No (Each) | 3436.9 | 10311
9 | 4 | sets | Supply and errection of GI stay set of dia 20mm,2.4 Mtr long stay rod and anchor plate 380mmX380mmX6.4mm including stay clams,turn buckle and GI stay wire tight end through strain insulator including excavation of pit and CC work etc., including cost of all materials and labour charges etc.,as directed by the Engineer-in-charge. | SS | 1set (Each set) | 2550.7 | 10203
10 | 100 | Rm | Supply and Transportation of Over Head 100 Sq mm AAA Conductor as per IS 398 (PART - II): 1996 including cost of all materials and labour charges etc.,as directed by the Engineer-in-charge. | SS | 1 Rm (One Running Meter) | 116.2 | 11620
11 | 3 | Sets | supply and fixing of 100 Amp, 11 KV Horn Gap fuse set as per IS 9358 on existing DP structure with 6 Nos of 24 KV/22 KV post insulators (IS 5350,Hot dipped Hardware,fuse wire of required size etc., including cost of all materials and labour charges etc.,as directed by the Engineer-in-charge. | SS | 1set (Each set) | 7561.1 | 22683
12 | 9 | Nos | Supply and fixing of 11 KV pin Insulator (IS 731/ 1971) with minimum creepage distance of 300 mm on existing cross arm including all accessories like Hot dip GI spindle and nuts etc., | SS | 1No (Each) | 250 | 2250
13 |  |  | PAINTING to new steel structure Two coats with aluminium paint in addition to priming coat (1 coat of redoxide primer) total 3 coats of approved quality including preparation of the surface, cost of brushes, cost and conveyance of all labour and materials, etc.at site of work complete as directed by the Engineer-in-Charge.
a | 10 | Sqm | Upto a height of 3.66m |  | 1 Sqm ( One square metre) | 205.8 | 2058
b | 40 | Sqm | For RS Joist poles to an height of 3.66m to 7.30m |  | 1 Sqm ( One square metre) | 256.2 | 10248
14 |  |  | Supply, Transportation, Installation, Testing and Commissioning of 11/0.433 500KVA copper wound TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per Energy Efficiency Level - 2 at basic Insulation level conforming to ISS 2026 (Part- I to Part - II) with latest ammended and as per IS 1180 Part-I : 2014 latest ammended, OLTC with initial filling of oil as per IS 335-1993. including cost of all materials and labour charges etc.,as directed by the Engineer-in-charge.The basic details of the Transformer are as under.
1. Quantity : 1 2. Rated KVA: 500KVA 3. Service & Location: Continuous Outdoor Distribution Transformer 4. Mounting: Plinth. 5. Wound: Copper Double wound 6. Type: Core type oil immersed 7. Cooling: ONAN 8. Temp Rise: 40⁰C in oil, 45⁰C by resistance 9. Vector Group: Dyn 11 10. Primary Connection: Delta 11. Nominal Voltage / Current: _ 12. Highest system Voltage: 12000V 13. Primary Frequency :50 HZ +/- 3% 14. Number of Phases: 3 15. Primary wires: 3 16. Secondary connection: Star 17. Secondary Volts / Current : 433V 18. Secondary phases: 3 19. Secondary wires: 4 20. Taps on primary winding for primary voltage variation: +5% to - 10% in steps of 2.5% of 7 position (6 Steps)
21. Terminal arrangement. a. HV: HT terminal box as per the site condition. b. LV: Cable box suitable to receive ---------- --Sq.mm XLPE cable 22. LV: One separate terminal for earthing. 23. Total Losses at 50% Loading [Watts] [Max] --- as per IS 24. Total Losses at 100% Loading [Watts] [Max]--- as per IS 25.Percentage Impedance at 75 deg. C at -----as per IS 26. No Load current: Less than 2% of full load current. 27. Standard Fittings & Accessories. a. Rating and terminal marking plate: One b. Lifting Lugs: Two c. Off-circuit tap switch: One. d. Earthing Terminals : Two e. Radiators (Attachable): Adequate f. Explosion vent with Diaphragm : One g. Conservator with Drain plug: one h. Oil filling hole with cap :One i. Oil level indicator: One j. Dehydrating Silica gel Breather: One k. Terminal Arrangement: HV With Terminal Box l. Terminal Arrangement: LV Cable Box
| 1 | No | m. Separate Neutral Bushing : One n. Drain cum filter valve with blanking plate: One o. Air release device: One p. Thermometer Pocket: One q. Four: Unidirectional flat rollers r. One :10Cm dial thermometer (Rigid stem type) | SS | 1No (Each) | 1881836 | 1881836
15 | 1 | No | Supply, testting, transport and errection of 11KV, 800 Amps, 25kA outdoor type VCB panel with current, voltage sensors and sensore operated relays sutable alluminium bus bar with PVC sleeves, with IP 54 protection including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 484500 | 484500
16 | 8 | Nos | Supply and Making heat shrinkable type outdoor termination joint kit of approved make suitable for XLPE insulated 11 KV cable, with required components, prepration of cable ends, testing etc.as required suitable for 3core 70/95 Sqmm cable including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.. | SS | 1No (Each) | 15157.4 | 121259
17 |  |  | Supply and Transportation of XLPE insulated IS:7098/II/85 H.T. cable for working voltage 11 KV Earthed with Stranded Compacted Circular Aluminium Conductor Screened with Extruded Semi-conducting compound, XLPE Insulated Screened with extruded semi-conducting compound in combination with Copper Tape, cores laid up, inner sheath of Thermoplastic tape, galvanized flat steel strip armoured and overall Extruded PVC Type ST- 2 Outer Sheathed cable etc., complete. Makes: As per list of recommended brands.
| 75 | Rm | 3C X 95 Sq mm | SS | 1 Rm (One Running Meter) | 1271.4 | 95355
18 |  |  | Supply and transportation of following XLPE insulated ,1100 volts grade armoured aluminium cable as per specification confirming to IS:7098 (part-1)./1554-I including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
a | 110 | Rm | 400 sqmm X 3.5 core XPLE Aluminium 1100v grade UG cable | SS | 1 Rm (One Running Meter) | 2823.3 | 310563
b | 30 | Rm | 10 sqmm X 4 core XPLE Aluminium 1100v grade UG cable | SS | 1 Rm (One Running Meter) | 195.4 | 5862
c | 100 | Rm | 6 sqmm X 2 core Aluminium 1100v Grade UG cable | SS | 1 Rm (One Running Meter) | 125 | 12500
19 |  |  | Labour charges for run of U.G cable on wall / existing pipe with necessary fixing arrangements such as saddles,clamps, wooden separators etc., including cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge.
a | 110 | Rm | UG cable Run in existing pipe/trench above 50 sq mm | SS | 1 Rm (One Running Meter) | 47.4 | 5214
b | 100 | Rm | UG cable Run in existing pipe/trench up to 50 sq mm | SS | 1 Rm (One Running Meter) | 47.4 | 4740
c | 30 | Rm | UG cable Run on wall up to 50 sqmm | SS | 1 Rm (One Running Meter) | 65.7 | 1971
20 |  |  | Supply and making one end termination with heavy duty double compression brass gland as per BS 6121:2005, IP 66 complete, SIBG type, heavy duty Aluminum lugs duly crimped with crimping tool, PVC tape etc., for following size of Armoured PVC insulated & PVC sheathed/ XLPE aluminum conductor cable of 1100 volt grade as required of size including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge..
| 2 | Nos | 3.5 core x 400 sq.mm | SS | 1No (Each) | 3299.4 | 6599
21 |  |  | Supply and laying of fallowing sizes Earth wire/strip in horizontal / vertical run in Ground / Recess including riviting,soldering, saddles,making connections etc., including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
a | 30 | Rm | 50mm X 6mm copper flat | SS | 1 Rm (One Running Meter) | 2794.9 | 83847
b | 125 | Rm | 50mm X 6mm GI flat | SS | 1 Rm (One Running Meter) | 236.3 | 29538
c | 25 | Rm | No.8 SWG GI wire | SS | 1 Rm (One Running Meter) | 11.4 | 285
d | 24 | Rm | 25mm X 3mm copper strip | SS | 1 Rm (One Running Meter) | 690.8 | 16579
22 | 4 | Nos | Providing independent earthing for sophisticated Electronic equipment with 600mm X 600mm X 3.15 mm thick copper plate rigidly fixed to 40mm dia 'B" class GI pipe of 2.5Rm. length and 0.3mtr length connected with reducer providing Gig funnel with wire mesh as per National Electric code and earth connection from electrode Copper strip to be bolted with nut bolts to GI pipe and providing 18" RCC collar providing staggered holes, filling with salt and charcoal from the bottom of the pipe giving earth connection from electrode with all accessories and labour charges complete as per IS specification 732/1982(Part-II) including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 18398.6 | 73594
23 | 10 | Nos | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I ( Cast iron ) pipe with Flange 2.5m long enclosed in C.C/ brick masonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with salt and charcoal from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 10310.6 | 103106
24 | 3 | Nos | Providing floor mounting stand for keeping 4 Nos of fire Bucket 1500mm length, 900mm height made out of 40X40X6mm Angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 1512.2 | 4537
25 | 12 | Nos | Supply of round bottom GI sheet bucket of 9Ltrs capacity as perIS:2546 made out of 24-gauge GI sheet with extra handle at bottom duly painted inside and red out side with printed with FIRE Mark for stand and hook and filled with sand and arrenged to existing stand or hook including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 371.5 | 4458
26 | 5 | Nos | Supply and fixing of Co2 type fire Exitinguishers 4.5 Kg Capacity confirming to IS:2878 made from ISI marked steam less cylinder confirming to IS:7285 & CE certified and fitted with ISI marked controlled valve confirming to IS: 3224, high pressure 1Mtr discharge hose& horn complete with intial gas charged with carrying handle with wheels and wall mounting braket.Squeez lever discharge, used un-used indicator,epoxy coated paint (Red) with 93% gloss with 2 years warrantyincluding cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 13838.3 | 69192
27 | 6 | Nos | Supply and fixing of Shock instruction chart in English/Hindi/ Telugu duly framed with front glass including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 662.4 | 3974
28 | 8 | Nos | Supply and fixing of cable root indicators of size 152 mm round/ 102mm X 102mm / 152mm x 152mm including cost and conveyance of all materials complete as directed. | SS | 1No (Each) | 125 | 1000
29 | 6 | Nos | Supply and fixing of Danger Notice plate size of 250 X 200mm including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 331.8 | 1991
30 | 2 | Nos | Supply of 11 KV/22 KV hand gloves including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 294.3 | 589
31 |  |  | Supply and run of following size 'B' class medium grade properties and weight as IS 1239 ISI mark with GI fittings with necessary accesories including all incidental and operational charges, cost and conveyance of all labour and materials etc., complete as directed by Engineer in charge.
a | 5 | Rm | 25 mm dia 'B' Class GI pipe | SS | 1 Rm (One Running Meter) | 413.6 | 2068
b | 5 | Rm | 40 mm dia 'B' Class GI pipe | SS | 1 Rm (One Running Meter) | 568 | 2840
c | 24 | Rm | 65 mm dia 'B' Class GI pipe | SS | 1 Rm (One Running Meter) | 850 | 20400
32 |  |  | Supply and run of following FRLS/ FRLS-H PVC insulated 1100 volts grade as per IS694/1990 specification for copper cable in existing pipe for mains including all incidental and operational charges, cost and conveyance of all labour and materials etc., complete as directed by Engineer in charge.
a | 15 | Rm | 2 of 4.0 sq mm copper wire | SS | 1 Rm (One Running Meter) | 162.1 | 2432
b | 5 | Rm | 2 of 6.0 sqmm copper wire | SS | 1 Rm (One Running Meter) | 222.9 | 1115
c | 75 | Rm | 2 of 1.0 sq mm copper wire | SS | 1 Rm (One Running Meter) | 64 | 4800
d | 10 | Rm | 2 of 2.5 sq mm copper wire | SS | 1 Rm (One Running Meter) | 106.8 | 1068
e | 10 | Rm | 1 of 2.5 sq mm copper wire | SS | 1 Rm (One Running Meter) | 53.5 | 535
33 |  |  | Supply and Fixing of ISI marked Following outer dia, 2.10 - 2.30 mm thickness medium grade, with IS9537 part3 rigid Surface PVC conduit pipe with all accessories fixing on Chromium plated metallic base saddles including all labour charges, etc., complete for run of mains as directed by Engineer in charge.
a | 25 | Rm | 63mm outer dia, 2.10 - 2.30 mm thickes Surface PVC conduit pipe | SS | 1 Rm (One Running Meter) | 206.1 | 5153
b | 75 | Rm | 20mm outer dia,1.40-1.55 mm thickness, Surface PVCconduit pipe | SS | 1 Rm (One Running Meter) | 111 | 8325
34 |  |  | Supply and fixing of the following double walled corrugated HDPE duct made as per specification BSEN-500 86/IS 14930 part-II.including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
a | 100 | Rm | outer dia 50mm and inner dia 38mm HDPE pipe | SS | 1 Rm (One Running Meter) | 187.5 | 18750
b | 30 | Rm | Outer dia 200mm and inner dia 170 mm | SS | 1 Rm (One Running Meter) | 876 | 26280
35 | 1 | No | Supply and fixing of 4way TPNDB of IP-43(Vertical) suitable for 4 pole Isolator and 12 Nos SPMCB's including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 11355.5 | 11356
36 |  |  | Supply and fixing of following Isolater / TP MCB /SP MCB in existing DB including all incidental and operational charges, cost and conveyance of all labour and materials etc., complete as directed by Engineer in charge.
a | 1 | No | 40 Amps 4 Pole Isolater | SS | 1No (Each) | 1283.5 | 1284
b | 6 | No | 6 - 32 Amp SP MCB | SS | 1No (Each) | 354.9 | 2129
c | 2 | Nos | 6-32 Amp TP MCB C/D curve | SS | 1No (Each) | 1441.3 | 2883
37 | 7 | Nos | Supply ,transportation and fixing of 90/100 LED Flood light Luminaire made of pressure diecast aluminum housing with powder coated, havingprotective toughened glass, supply Input voltage 120 - 270 V AC, P.F >0.90, high power LEDs, with a System Efficacy >=120 lumens/watt andjunction temperature < 70°C, with ingress protection IP66, Luminaireperformance complies to IS 10322 (Part 5 / Sec-5), IK05, driver surgeprotection 4KV, In-house additional surge protection ≥ 10KV with wide/narrow beam optics, THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete with earthconnection and not less than two years warranty.including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 8654.1 | 60579
38 | 3 | Nos | Supply, transportation and fixing of 90W LED Street light Luminaire made of pressure diecast aluminum body with powder coated, having protective toughened glass / temperature protective polycarbonate diffuser, supply input voltage 120 - 270V AC, P.F > 0.90, high power LEDs having System Efficacy >= 120 lumens/watt and junction temperature < 70°C, with Ingress protection IP66, Luminaire performance complies to IS 10322 (Part 5/Sec3), driver surge protection 4KV, in-house additional Surge protection 10 KV with optics distribution, THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete with earth connection and not less than two years warranty. including cost labour chargers for fixing with GI pipeof all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 8176.9 | 24531
39 | 2 | Nos | Supply and fixing of 6''X8'' Teak Wood board with 3mm thick hylam sheet,screws,rawal plugs including all incidental and operational charges, cost and conveyance of all labour and materials etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 160.5 | 321
40 | 2 | Nos | Supply and fixing of 6A, 3/2 pin flush type socket with shutter and 6 Amp switch control on a common switch board with earth continuity including wire leads, earth connections along with all labour charges,etc.,complete as directed by Engineer in charge. | SS | 1No (Each) | 186.4 | 373
41 | 2 | Nos | Supply and fixing ISI marked of 32A, 240V DP Flush type switch including cost and conveyance of all labour charges, etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 213.9 | 428
42 | 20 | sqm | Supply installation testing and commissioning of free standing floor mounted dust and vermin proof compart mentalised cubical panel made out of CRCA sheet, required hardware, duly painted by two coats of zinc / red oxide primer followed by Powder coated / epoxy / PU painted with phosphatisation in grey or required shade after rinsing.The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable, gland plate M.S base channel, hinged door with locking arrangement for equipment / switchgear thickness of sheet shall not be less than 1.6mm up to 600mm length/width of any compartment and be of 2.0mm above 600mm. Load bearing structure shall be of 2.0mm thick sheet supported by base MS channel if required.Side walls and cable alley compartment having bolted type doors with detachable extension type stucture (only outer area on all sides shall be measured and panel to be abricated from CPRI approved fabricator) including cost and conveyance of all labour and materials , all incidental and operational charges etc., complete as directed by Engineer in charge. | SS | 1Sqm (One square metre) | 6346.5 | 126930
43 |  |  | Supply of Air Circuit Breaker confirms to IS 13947-2, IEC 60947-2 and BS-EN 60947 with Micro processer based having overload, shot circuit and earth fault protection with display and 20 faults History backup with BMS compatible communication ports including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
| 1 | No | 800A, 4 Pole, 50kA electrically operated, manually draw out type | SS | 1No (Each) | 227845.8 | 227846
44 |  |  | Supply and fixing of adjustable, confirms to IEC 60947-2 and IS 13947-Part 1 & 2, having Breaking Capacity with thermal magnetic release Panel Mounted including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
a | 2 | Nos | 630A 4 Pole MCCB,50 KA | SS | 1No (Each) | 52500.3 | 105001
b | 1 | Nos | 250 4 Pole MCCB,36/35 KA | SS | 1No (Each) | 29061.6 | 29062
c | 1 | Nos | 125A 4 Pole MCCB,25KA | SS | 1No (Each) | 12599.2 | 12599
45 | 1 | Nos | Supply and fixing of CT operated direct reading type Above 500A Digital Ammeter on existing panel, making connection by PVC insulated copper conductor with PVC sleeves / channel etc. including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 2374.6 | 2375
46 | 1 | Nos | Supply and fixing of (0-500) V range Digital type Voltmeter on existing panel, making connection by PVC insulated copper conductor with PVC sleeves / channel etc. including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 2374.6 | 2375
47 | 3 | Nos | Supply and Fixing of Current Transformer, from 500 / 5 to 1600/5 Ratio, 15 VA, class 1 accuracy with all necessary support in existing panel including connection etc. including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 1187.3 | 3562
48 | 1 | Nos | Supply , Transportation and fixing of energy analyzer (multi-function energy meter) with LCD/LED display capable of minimum 20 numbers electrical parameters display with 1A/5A CT input for LV/ HV network, RS 485 communication port etc. including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 13122.5 | 13123
49 | 1 | Job | Supply transportation Testing and instalation of 100 KVAR APFC Panel with sutable line switches TPMCBs/SPMCBs and relays with CRCA sheet(14/16 SWG) including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1Job (One Job) | 176460 | 176460
50 |  |  | Supply and fixing of bus bar by means of SMC / DMC type insulator, high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge.
a | 50 | Kgs | Electrolytic grade aluminum bus bar | SS | 1 KG ( One Kilo gram) | 532.9 | 26645
b | 5 | Kgs | Electrolytic grade copper bus bar | SS | 1 KG ( One Kilo gram) | 1124.8 | 5624
51 | 16 | Nos | Supply and making end termination with 400 sqmm heavy aluminium lugs (pin/ring type ) as per specification duly crimped with crimping tool, PVC tape etc. including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 234 | 3744
52 | 6 | sqm | Supply and fixing of PVC synthetic elastomer electrically insulated at conforming to IS: 15652-2006 with class A insulation having 2mm thickness up to 3.3 KV including cost and conveyance of all labour and materials , all incidental and operational charges etc., complete as directed by Engineer in charge. | SS | 1Sqm (One square metre) | 5224 | 31344
53 | 4 | Nos | Wiring with 2 runs of 1.0 Sq.mm ISI marked FRLS/FRLS-H/ZHFR/HFFR, P.V.C insulated flexible copper cables 1100V grade as per IS :694/1990 & IS 17048 /2018 in existing pipe with 6A switch, 3plate jumbo Ceiling rose and 3mm thick Hylam sheet covering to switch control box including all labour charges, etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings as including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1No (Each) | 712.9 | 2852
54 | 2 | Nos | Supply & fixing of 1x 20 watts Retrofit Tube light with alluminium anadised body on wall / Ceiling with TW round blocks with all accessories including giving connections cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 1076.2 | 2152
55 | 1 | Nos | Supply and fixing of 48"(1200mm) sweep 5 star rated BLDC Ceiling Fan with double ball bearings, input voltage 230V, AC converted to 24V DC, Power input not more than 30W, air delivery not less than 220 cubic mtr /min and minimum service value of 7.0, with remote and with out Regulator, including giving connections cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 4222.4 | 4222
56 | 1 | Nos | Supply and erecting of fan D-hook in RCC roof slab by drilling the slab with machine, including cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 247.4 | 247
57 | 1 | Rm | Supply of 19/20 mm steel tube fan down rod including cost of all necessary materials and convenece charges etc, as directed by the Engineer-in-charge. | SS | 1 Rm (One Running Meter) | 135.2 | 135
58 | 1 | Job | Labour charges for 19/20mm steel tube down rod with bolts & nuts duly painted with matching colour of fan complete, including giving connections cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge. | SS | 1 Job (One Job) | 90.7 | 91
59 | 1 | Nos | Supply and fixing of 12"(300mm) Heavy duty Exhaust fans in existing hole / frame or in the wall with necessary connections and including giving connections cost and conveyance of all labour charges, materials etc., complete as directed by Engineer in charge. | SS | 1No (Each) | 4413.88 | 4414
60 |  |  | Supply and fixing of extended rotating handle suitable for the following 4 pole 415V MCCBs including cost of trnsporatation and labour charges etc, including cost and conveyance of all labiur and materials, all incidental and operational charges etc, complete as directed by engineer in charge
a | 2 | Nos | 250A/415V 4Pole MCCB | SS | 1No (Each) | 3240 | 6480
b | 2 | Nos | 630A/415V 4Pole MCCB | SS | 1No (Each) | 3960 | 7920
61 | 1 | Job | Job chart for the CEIG approval : 1) preparation schematic single line diagram(SLD) and physical lay out interpolating in the e Bus Depot lay out for submission to CEIG, by inspecting the site. 2) submission of application to CEIG along with drawings and required documents for getting approval from CEIG including the necessary inspection charges and expenses 3)Arranging final inspection by the CEIG duly submitting the required particulars such as list of load particulars and test certificates of material testing equipment, including 'A' grade licensed contractors WRO-1,WRO-2 reports. After inspection, preparation of compliance reports for the defects noticed for getting statutory approval from the CEIG. 4) Payment of Government treasury challan for drawing approvals and inspection of installation. 5) submission of hard copies of approved drawings and documents submitted to CEIG and soft copies for record. 6) Preparation of Big size photo frame with CEIG approved drawing. 7) Co-ordination with CEIG officials, Electrical contractor of APSRTC works and Engineers of APSRTC. | SS | 1 Job (One Job) | 80000 | 80000
|  |  | ESTIMATED CONTRACT VALUE (ECV) |  |  |  | 4702869
(Rupees Fourty seven lakhs two thousand eight hundred sixty nine only)

## Seign
SCHEDULE 'A' - PART - 1B
Name of work: Providing Electrical Infrastructure to Intermediate Charging Station at Adoni Bus Station, Kurnool District (3rd Call).
Sl. No. | Description of Item | Estimate amount in Rupees ( Figures and Words )
1 | Provision towards Seingniorage Charges | NIL
NOTE : The premium or discount quoted by the contractor will be applicable only for working items in Schedule 'A'Part-I
However the provisions contained in Schedule 'A' Part-IB above will be excluding the ECV amount.
BIDDER TENDER INVITING AUTHOURITY

## Part II
SCHEDULE- A (PART II)
Name of work: Providing Electrical Infrastructure to Intermediate Charging Station at Adoni Bus Station, Kurnool District (3rd Call).
Sl No | Description of Work | Estiamted amount in Rupees (Figures and Words)
1 | 2 | 3
1 | Provision towards the GST charges @ 18% | 847363
(Rupees Eight lakhs forty seven thousand three hundred and sixty three only)
NOTE : The premium or discount by the contractor will be applicable only for working items in schedule 'A' (Part-I). However the provisions contained in Schedule 'A' (Part IB & PART- II) above will be excluding the ECV amount
Note : The Bidder should submit the proof of updated GST clearance certificate
BIDDER |  | TENDER INVITING AUTHORITY