## abs
ABSTRACT
Name of the Work : Replacement of existing ACSR Lynx conductor (16.37KM) with AAAC Panther conductor for 132KV Chittoor – Pakala SC line in Chittoor District under RMI 2024-25 on turn key basis
SL No | DESCRIPTION | Basic Cost
Line
A | Material portion
| Schedule-A (Electrical-Line) | 16805433.16
| Total Schedule-A | 16805433.16
B | Labour Portion
| Schedule-B (Electrical-Line) | 5207680.96
| Total Schedule-B | 5207680.96
| Grand Total | 22013114
CHIEF ENGINEER/ZONE KADAPA :: APTRANSCO

## Sch-A
SCHEDULE-A
Name of the Work : Replacement of existing ACSR Lynx conductor (16.37KM) with AAAC Panther conductor for 132KV Chittoor – Pakala SC line in Chittoor District under RMI 2024-25 on turn key basis
Sl. No | Particulars | Qty | UOM | Total Unit rate of Material (in Rs.) | Total Amount (in Rs.)
1 | AAAC Panther Conductor | 55 | KM | 268744.51 | 14780948.05 |  | aRMOUR GRIP SUSPENSION
2 | Single Suspension H/W (AGS-FAH) AAAC Panther | 140 | Nos. | 2642.98 | 370017.2 | AGS-FAH | FIXED ARCHING HORN
3 | Double suspension H/W (AGS type) for AAAC Panther | 17 | Nos. | 5512.56 | 93713.52
4 | Single Tension Hardware for AAAC Panther | 61 | Nos. | 2607.96 | 159085.56 | different in hard copy quantities
5 | Double Tension Hardware for AAAC Panther | 7 | Nos. | 5578.48 | 39049.36
6 | Midspan Joints for AAAC Panther | 75 | Nos. | 708.64 | 53148
7 | Repair Sleeves for AAAC Panther | 30 | Nos. | 296.64 | 8899.2
8 | Vibration dampers for AAAC Panther | 384 | Nos. | 710.7 | 272908.8
9 | 132KV,70 KN SRC Insulators | 174 | Nos. | 3155.92 | 549130.08
10 | 132KV,120KN SRC Insulators | 74 | Nos. | 3392.82 | 251068.68
11 | Supply and fixing GI flexible earth bonds | 25 | Nos. | 339.9 | 8497.5
12 | Danger Boards with bolts,nuts & washers | 57 | Nos. | 260.59 | 14853.63
13 | Phase plates | 57 | Nos. | 265.74 | 15147.18
14 | Anti climbing devices | 4 | Nos. | 3998.46 | 15993.84
15 | Supply of GI Tower parts including cost of Steel, Galvanisation, Fabrication and Transportation to Site | 1 | MT | 126679.72 | 126679.72
16 | Supply of GI bolts & Nuts | 0.1 | MT | 119458.37 | 11945.84
17 | Supply of 75x8 GI flat | 60 | RM | 462.61 | 27756.6
18 | 7/3.15mm Earth wire | 160 | RM | 41.19 | 6590.4
Sub-Total in Rs. |  |  |  |  | 16805433.16
CHIEF ENGINEER/ZONE
KADAPA :: APTRANSCO

## Sch-B
SCHEDULE:B
Name of the Work : Replacement of existing ACSR Lynx conductor (16.37KM) with AAAC Panther conductor for 132KV Chittoor – Pakala SC line in Chittoor District under RMI 2024-25
(All financial figures are in Rs.)
S. No. | Description | Qty. | UOM | Unit Rate of Labour | Total of Labour
1 | 3 | 4 | 5 | 10 | 11
1 | Dimantling of power conductor: Dismantling of tension insulators and suspension insulators, paving out the conductor, rough sagging, jointing, tensioning, clipping and fixing of preformed armour rods and vibration dampers, measuring ground clearances wherever necessary. Which excludes the works involved in the crossing of LT, 11 KV & 33 KV power lines viz dismantling and restringing of conductor
| 3 Nos Lynx Conductors ( Dismantling Under Shutdown ) | 16.37 | Km | 66690.8 | 1091728.396
2 | 3 Nos Lynx Conductors ( Dismantling Under 1 st Ckt Live condition Pakala-K.P.Mitta feeder & Chittoor-Irala feeder) | 0.445 | Km | 75771.05 | 33718.1173
3 | STRINGING OF POWER CONDUCTOR: Hoisting of tension insulators and Suspension insulators, paving out the conductor, rough sagging, Jointing, tensioning, clipping and fixing of preformed Armour rods and vibration dampers. measuring ground clearances wherever necessary. Which excludes the works involved in the crossing of LT, 11kV & 33kV power lines viz dismantling and restringing of conductor (Including transportation of materials from constractor site stores to work site) |  |  |  | 0
3a | 3 No.s AAAC Panther (Under Shutdown Condition) | 16.37 | KM | 104610.97 | 1712481.5789
3b | 3 No.s AAAC Panther (Under 1 st Ckt Live condition) | 0.445 | KM | 118854.22 | 52890.1279
4 | Earthing of towers including cost of Excavation, Back-filling, including cost of 25 mm dia 2.5 mm thick, class 'C' G.I. pipe of 3.00 Mtrs length,BH Coke , Salt etc., and measuring tower footing resistance. (Without GI Flat ) for counter poise earthing. | 6 | Nos | 9254.17 | 55525.02
5 | Counterpoise earthing including clamping devices and terminal lugs, Excluding cost of steel wire | 4 | Loc | 11637.87 | 46551.48
6 | Excavation of earth pit, putting cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long inside the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long inside the pit, backfill the pit in the 25mm size granules of BHcoke for full depth of the pit with alternate layers of BH coke and salt of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of BH coke, salt, clamps, C.I.Pipes and RCC collars, labour charges for all operational and incidental items of work etc., complete. including cost of 75x8 GI flat for 60m. (For Railway Crossing Towers) | 4 |  | 28286.3 | 113145.2 |  |  | 60
8 | Dismantling and re-stringing of 33 KV conductor for crossing of 33 KV lines during stringing of EHTlines | 60 | Conductor | 6151.63 | 369097.8
9 | Dismantling and re-stringing of 11 KV conductor for crossing of 11 KV lines during stringing of EHTlines | 120 | Conductor | 3365.76 | 403891.2
10 | Dismantling and re-stringing of LT line conductor/cables for crossing of LT lines during stringing of EHTlines | 240 | Conductor | 2119.13 | 508591.2
11 | Providing of vehicle to field officials for both Civil & Electrical | 10000 | KM | 9.98 | 99800
12 | Clearing heavy jungle | 50000 | Sq. Mtr | 7.4757 | 373785 | 5 km Forest
13 | Clearing light Jungle | 30000 | Sq. Mtr | 6.5412 | 196236
14 | Cutting and Removing Palmyrah trees including stacking of girth of 30 to 100 cm | 6 | Nos | 49.06 | 294.36
15 | Cutting and Removing Palmyrah trees including stacking of girth of 100 to 200 cm | 8 | Nos | 112.14 | 897.12
16 | Cutting and Removing other kind of trees including stacking of girth of 30 to 100 cm | 10 | Nos | 77.09 | 770.9
17 | Cutting and Removing other kind of trees including stacking of girth of 100 to 200 cm | 18 | Nos | 119.14 | 2144.52
18 | Cutting and Removing other kind of trees including stacking of girth of above 200 cm | 20 | Nos | 193.9 | 3878
19 | Transporting of dismantling materials from Line work site to Kadapa Stores ( Includinga allowances) | 6 | Loads | 15313.86 | 91883.16
20 | Loading and unloading charges of dismantled materials from site to stores | 1 | LS | 50371.78 | 50371.78 |  | 142254.94
5207680.96
5207680.96
CHIEF ENGINEER/ZONE
KADAPA :: APTRANSCO

## Sheet1 (hidden)
(As per Technical Sanction)
Annexure V - 132kV Substation Rangannagudem / Remalle (Krishna District) Estimate (Electrical ) - Labour Portion
Sl. No. | Master Sl.No. of SSR 2012-13 | Description | Qty. | UOM | Basic Rate of Labour as per SSR 2012-13 | Extra conditions - Dismantling /Shutdown (on 6) | Adj. Basic Rate | COP 14% on (8) | Insurance on material @ 0.5% | Unit Rate of Labour (8+9) | Unit rate of Material | Total of Labour (4 x 11) | Total of Material ( 4 x 12) | Total
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | ('10) | (11) | (12) | (13) | (14) | (15)
40 | Pg 17 item CS27 | Supply and installation of lighting fixures of 250 W HPSV of Crompton Greaves / Philips make on switch yard structures including cost of lighting fixtures,cabling and connections. | 30 | Nos. | 867 | 0 | 867 | 121.38 |  | 988.38 | 6000 | 29651.4 | 180000 | 209651.4
[10 empty] | WCT: 5% on total of material |  | 9000
[10 empty] | Service tax:12.36% on total of labour |  | 3664.91
[10 empty] | Labour cess: 1% on total of labour+ Material |  | 2096.51
[10 empty] | Total with taxes |  | 44412.82
[10 empty] | Total of Labour & Material |  | 224412.82
Proposed As per JMD Instruction
40(a) | Pg 17 item CS27 | Supply and installation of lighting fixures of 250 W HPSV of Crompton Greaves / Philips make on switch yard structures including cost of lighting fixtures,cabling and connections and also including 40mm dia GI Bent pipe of 0.75Mts length with suitable clamps for fixing to sltructures in complete shape. | 6 | Nos. | 867 | 0 | 867 | 121.38 |  | 988.38 | 6000 | 5930.28 | 36000 | 41930.28
40(b) | As per field estimate | Supply, installing , testing and Commissioning of 80 W LED lamps along with fixtures for switchyard lighting in Substations. | 25 | Nos. | This includes both labour and material cost | [5 empty] | 12768 | 0 | 319200 | 319200
[12 empty] | 5930.28 | 355200 | 361130.28
[10 empty] | WCT: 5% on total of material |  | 17760
[10 empty] | Service tax:12.36% on total of labour |  | 732.98
[10 empty] | Labour cess: 1% on total of labour+ Material |  | 3611.3
[10 empty] | Total with taxes |  | 28034.56
[10 empty] | Total of Labour & Material |  | 383234.56
|  | Difference in cost | =Rs. | 158821.74
CHIEF ENGINEER
CONSTRUCTION-II
CHIEF ENGINEER
CONSTRUCTION-II
//FORWARDED BY ORDER //
ASST. DIVISIONAL ENGINEER (ELECL.)
// FORWARDED BY ORDER //
ASST.DIVISIONAL ENGINEER/Elecl.
CHIEF ENGINEER
CONSTRUCTION-II

## comparatative (hidden)
COMPARATIVE STATEMENT
#REF!
Quotation Given by
Sl. No | Description of work | Per | M/s Shasi Cables limited, Lucknow | M/s JSK Industries Pvt Ltd.,,Mumbai | M/s Oswal cables Pvt Ltd., Jaipur,Rajasthan | M/s Aumni Transmission Industry Pvt Ltd.,Vadodara
1 | High Temperature low sag (HTLS) ACSS Conductor Equivalent to Lynx Conductor | 1 KM | 260000 | 213371.25 | 270000 | ...
2 | Single Suspension Hard ware (SSHW) for HTLS Euivalent to Lynx Conductor | 1 No | ... | 5600 | ... | 2067
3 | Double Suspension Hard ware (DSHW) for HTLS Euivalent to Lynx Conductor | 1 No | ... | 9600 | ... | 4456
4 | Single Tension Hard ware (STHW) For HTLS Equivalent to Lynx Conductor | 1 No | ... | 6720 | ... | 1931
5 | Double tension Hard Ware (DTHW) For HTLS Equivalent to Lynx Conductor | 1 No | ... | 11520 | ... | 3800
6 | Mid Span Compression Joints for HTLS Equivalent to Lynx Conductor | 1 No | ... | 2560 | ... | 471
7 | Repair Sleeves for HTLS Equivalent to Lynx Conductor | 1 No | ... | 1760 | ... | 155
8 | Vibration Dampers for HTLS Equivalent to Lynx Conductor | 1 No | ... | 2000 | ... | 388
9 | Armour Rods for HTLS Equivalent to Lynx Conductor | 1 No | ... | ... | ... | 619